## Space Based Calculation
Roof Length | L_roof | 30000 | mm
Roof Width | W_roof | 38500 | mm
Panel Length | L_panel | 2278 | mm
Panel Width | W_panel | 1134 | mm
Distance between row | D_r | 10 | mm
Distance between column | D_c | 1000 | mm
PV panel power | P_pv | 590 | W
Landsacpe
N_across | 9 | nos
N_up | 33 | nos
N_panel | 297 | nos
Potrait
N_across | 14 | nos
N_up | 16 | nos
N_panel | 224 | nos
Summary
Optimum Orientation | Landsacpe
Optimum panel number | 297 | nos
System power | 175.23 | kWp
Proceed to "Inverter Sizing" tab for final system configuration

## Inverter Sizing
| Inverter No | 1 |  |  |  |  | Inverter No | 2
| Inverter Model | SUN2000-100KTL-M2 |  |  |  |  | Inverter Model | SUN2000-50KTL-M3
| Panel Model | Jinko JKM590N-72HL4 |  |  |  |  | Panel Model | Jinko JKM590N-72HL4
| Panel Parameter | [5 empty] | Panel Parameter
| DATA |  | VALUE |  |  |  | DATA |  | VALUE
| PV panel max power | Pmax_stc | 590 | W |  |  | PV panel max power | Pmax_stc | 590 | W
| PV panel open circuit voltage | Voc_stc | 52.63 | V |  |  | PV panel open circuit voltage | Voc_stc | 52.63 | V
| PV panel max power voltage | Vpmax_stc | 43.71 | V |  |  | PV panel max power voltage | Vpmax_stc | 43.71 | V
| Maximum System Voltage | Vsys_max_pv | 1500 | V |  |  | Maximum System Voltage | Vsys_max_pv | 1500 | V
| PV panel short circuit current | Isc_stc | 14.13 | A |  |  | PV panel short circuit current | Isc_stc | 14.13 | A
| PV panel max power current | Ipmax_stc | 13.5 | A |  |  | PV panel max power current | Ipmax_stc | 13.5 | A
| Temperature coefficient of Voc | βvoc | -0.25 | %/◦C |  |  | Temperature coefficient of Voc | βvoc | -0.25 | %/◦C
| Temperature coefficient of Pmax | ϒpmax | -0.29 | %/◦C |  |  | Temperature coefficient of Pmax | ϒpmax | -0.29 | %/◦C
| Inverter Parameter | [5 empty] | Inverter Parameter
| Rated AC Active Power | Pmax | 100 | kW |  |  | Rated AC Active Power | Pmax | 50 | kW
| Absolute maximum input voltage | Vmax_abs_inv | 1100 | V |  |  | Absolute maximum input voltage | Vmax_abs_inv | 1100 | V
| Maximum MPPT voltage | Vmax_mppt | 1000 | V |  |  | Maximum MPPT voltage | Vmax_mppt | 1000 | V
| Minimum MPPT voltage | Vmin_mppt | 200 | V |  |  | Minimum MPPT voltage | Vmin_mppt | 200 | V
| Minimum start Voltage | Vstart_inv | 200 | V |  |  | Minimum start Voltage | Vstart_inv | 200 | V
| Rated input Voltage | Vrated_inv | 600 | V |  |  | Rated input Voltage | Vrated_inv | 600 | V
| Maximum short circuit current per MPPT | Isc_max_mppt | 40 | A |  |  | Maximum short circuit current per MPPT | Isc_max_mppt | 40 | A
| Number of MPP Tracker | N_mppt | 10 |  |  |  | Number of MPP Tracker | N_mppt | 4
| Number of Inputs | N_mppt_input | 2 |  |  |  | Number of Inputs | N_mppt_input | 8
| Operating Parameter | [5 empty] | Operating Parameter
| Safety factor | sf1 | 1.25 |  |  |  | Safety factor | sf1 | 1.25
| DC cable efficiency | π_cable | 0.97 |  |  |  | DC cable efficiency | π_cable | 0.97
| Maximum module temperature | Tmod_max | 85 | ◦C |  |  | Maximum module temperature | Tmod_max | 85 | ◦C
| Minimum module temperature | Tmod_min | 20 | ◦C |  |  | Minimum module temperature | Tmod_min | 20 | ◦C
| STC temperature | Tstc | 25 | ◦C |  |  | STC temperature | Tstc | 25 | ◦C
| Number of Panel Calculation | [5 empty] | Number of Panel Calculation
| Maximum open circuit voltage | Voc_max | 53.2879 | V |  |  | Maximum open circuit voltage | Voc_max | 53.2879 | V
| Minimum open circuit voltage | Voc_min | 44.7355 | V |  |  | Minimum open circuit voltage | Voc_min | 44.7355 | V
| Maximum voltage at maximum power | Vpmax_max | 44.3438 | V |  |  | Maximum voltage at maximum power | Vpmax_max | 44.3438 | V
| Minimum voltage at maximum power | Vpmax_min | 36.1045 | V |  |  | Minimum voltage at maximum power | Vpmax_min | 36.1045 | V
Determine maximum number of panel per string | Max number based on max Voc | Ns_max_abs | 20 | modules |  |  | Max number based on max Voc | Ns_max_abs | 20 | modules
| Max number based on max Vpmax | Ns_max_mppt | 22 | modules |  |  | Max number based on max Vpmax | Ns_max_mppt | 22 | modules
| Max number based on Vsys | Ns_max_pv | 28 | modules |  |  | Max number based on Vsys | Ns_max_pv | 28 | modules
Determine minimum number of panel per string | Min number based on min Vpmax | Ns_min_mppt | 6 | modules |  |  | Min number based on min Vpmax | Ns_min_mppt | 6 | modules
| Min number based on min Voc | Ns_min_start | 5 | modules |  |  | Min number based on min Voc | Ns_min_start | 5 | modules
| Final Max number of panel per string | Ns_max | 20 | modules |  |  | Final Max number of panel per string | Ns_max | 20 | modules
| Final Min number of panel per string | Ns_min | 6 | modules |  |  | Final Min number of panel per string | Ns_min | 6 | modules
| Percentage of recommended operating window voltage | W% | 50 | % |  |  | Percentage of recommended operating window voltage | W% | 50 | %
Determine optimum number of panel per string | Min recommended number of panel per string | Ns_rec_min | 13 | modules |  |  | Min recommended number of panel per string | Ns_rec_min | 13 | modules
| Max recommended number of panel per string | Ns_rec_max | 13 | modules |  |  | Max recommended number of panel per string | Ns_rec_max | 13 | modules
| Recommended nmber of panel per string | Ns_rec | 13-13 | modules |  |  |  | Ns_rec | 13-13 | modules
Determine maximum number of strings per MPPT | Max number of strings per MPPT | Np_max_per_mppt | 2 | strings |  |  | Max number of strings per MPPT | Np_max_per_mppt | 2 | strings
| Number of panel per string and number of string calculation | [5 empty] | Number of panel per string and number of string calculation
| Estimated total number of panels per inverter | Nt | 190 | modules |  |  | Estimated total number of panels per inverter | Nt | 107 | modules
| Total module per MPPT | Nt_per_mppt | 19 | modules |  |  | Total module per MPPT | Nt_per_mppt | 26 | modules
| Total strings per MPPT | Np_per_mppt | 1 | string(s) |  |  | Total strings per MPPT | Np_per_mppt | 2 | string(s)
| Final Configuration | [5 empty] | Final Configuration
| Each MPPT with 19 number of panels, each MPPT has 2 input: | [5 empty] | Each MPPT with 26 number of panels, each MPPT has 8 input:
| MPPT Input A: 19 panels | [5 empty] | MPPT Input A: 13 panels
| MPPT Input B: Not in use | [5 empty] | MPPT Input B: 13 panels
| Final total number of PV panel per inverter | Nt | 190 | modules |  |  | Final total number of PV panel per inverter | Nt | 104 | modules
| Total kWp of PV system |  | 112.1 | kWp |  |  | Total kWp of PV system |  | 61.36 | kWp
| Final DC/AC ratio |  | 1.121 |  |  |  | Final DC/AC ratio |  | 1.2272
| Final string max open circuit voltage | Vstr_oc_max | 1012.4696 | < | 1100 | PASS | Final string max open circuit voltage | Vstr_oc_max | 692.7424 | < | 1100 | PASS
| Final string min open circuit voltage | Vstr_oc_min | 849.9745 | > | 200 | PASS | Final string min open circuit voltage | Vstr_oc_min | 581.5615 | > | 200 | PASS
| Final string max voltage at max power | Vstr_pmax_max | 842.5321 | < | 1000 | PASS | Final string max voltage at max power | Vstr_pmax_max | 576.4693 | < | 1000 | PASS
| Final string min voltage at max power | Vstr_pmax_min | 685.9847 | > | 200 | PASS | Final string min voltage at max power | Vstr_pmax_min | 469.358 | > | 200 | PASS
Note on D27: User: Safety factor: 1.25 according to Seda
Note on K27: User: Safety factor: 1.25 according to Seda
Note on D45: User: Assume 70% if Vrated is not provided
Note on K45: User: Assume 70% if Vrated is not provided

## Cable sizing
DC Cable
Max String Cable length | 100 | m | * Use the longest string cable
Copper | 0.017857 |  | * Select material of cable (Drop down)
Ipmax stc | 13.5 | A
Vpmax | 43.71 | V
Coeff Vpmax | -0.29 | %/◦C
Total panel per string | 13 | modules
Allowable Voltage drop | 3 | % | *If no Array, use 3%, If exist, separate String 2% and Array 1%
Max Panel Temperature | 85 | ◦C | * For Malaysia, use 70 degree celcius
Min Cable Size | 4.3675 | mm2
Final Cable Size | 6 | mm2
Voltage Drop | 10.0446 | V
Voltage Drop % | 1.3248 | %
AC (Single phase)
Inverter Rated Power | 50 | kW
Inverter Rated Output Current | 72.2 | A
Max Cable Length | 150 | m
Copper | 0.017857
PF | 0.85
Allowable Voltage Drop | 3 | %
Nominal Voltage | 230 | V
Min Cable Size | 48 | mm2
AC (Three phase)
Inverter Rated Power | 50 | kW
Inverter Rated Output Current | 72.2 | A
Max Cable Length | 150 | m
Copper | 0.017857
PF | 0.85
Allowable Voltage Drop | 3 | %
Nominal Voltage | 400 | V
Min Cable Size | 48 | mm2
|  |  | 0.826 |  | 16.5441 | V
568.23
551.6859
Copper | 0.017857 |  |  |  | 2.912%
Alluminium | 0.029412
|  | min | max | output
|  | 0 | 2.5 | 2.5
|  | 2.501 | 4 | 4
|  | 4.001 | 6 | 6
|  | 6.001 | 10 | 10